SmokeShield™ Fire & Smoke SPECIFICATION

Section 08 3483

Fire & Smoke door containment system

PART 1 - General

## Summary

### Section Includes: Smoke detector activated Fire & Smoke door smoke containment curtain and control system designed seal the hoistway opening.

### Products Supplied But Not Installed Under This Section:

#### End-of-line diode (3.9V, 2W). Installed at smoke detector to monitor the circuit.

### Related Sections:

#### 09 2200Non-Load Bearing Wall Framing: Metal backing in housing mounting area.

#### 09 9100Paints: Field painting of specified components; repainting of existing field painted Fire & Smoke door frames.

#### 28 3000Detection and Alarm: Provisions for smoke detectors.

#### Division 26 Sections for 120VAC and control circuit power including conduit, boxes, conductors, wiring devices, and emergency power.

## References

### NFPA Codes and Standards:

#### 70  National Electrical Code.

#### 105  Recommended Practice for the Installation of Smoke-Control Door Assemblies.

#### 72-2002 and 2007 – National Fire Alarm Code

#### 80 – Standard for Fire Doors and Other Opening Protectives

### International Building Code

#### 2003.

#### 2006

#### 2009

#### 2012

#### 2015

### UL Standards:

#### 268  Smoke Detectors for Fire Protective Signaling Systems.

#### 508  Industrial Control Equipment.

#### 864  Control Units for Fire Protective Signaling Systems.

#### 1784  Air Leakage Tests for Door Assemblies.

## Submittals

### Reference Section 01 3300Submittal Procedures; submit following items:

#### Product Data.

#### Shop Drawings: Include door width and height, jamb width, jamb and head projection, curtain width, mounting height, and housing width. Show and identify related work performed under other sections of the specifications.

#### Quality Assurance/Control Submittals:

##### Qualifications:

###### Proof of manufacturer qualifications.

###### Proof of Installer qualifications.

##### Certifications: Copy of specified items.

##### Manufacturer’s installation instructions and testing procedures

## Closeout Submittals

### Comply Section 01 7700Closeout Submittals; submit following items:

#### Operation and Maintenance Manual

#### Manufacturer’s Warranties

## Quality Assurance

### Overall Standards:

#### Manufacturer shall maintain a quality control program in accordance with ISO 9001:2008.

#### Manufacturer shall maintain an in-plant UL follow up inspection procedure.

### Qualifications:

#### Manufacturer Qualifications: Minimum ten years’ experience in producing smoke and fire protection closures.

#### Installer Qualifications: Factory approved by manufacturer.

### Certifications:

#### Proof of compliance with:

##### NFPA 105

#### Underwriters Laboratories

##### UL Standard 10D 3hr Listing Label

##### UL standard 1784 Listing Label

##### ASTM E84 Listing Label

### Pre-Installation Meeting:

#### Schedule and convene a pre-installation meeting prior to commencement of field operations with representatives of the following in attendance: Owner, Architect, General Contractor, smoke containment system sub-contractor, painting sub-contractor, and electrical sub-contractor.

#### Review substrate conditions, requirements of related work, installation instructions, storage and handling procedures, and protection measures.

#### Keep minutes of meeting including responsibilities of various parties and deviations from specifications or installation instructions.

## Delivery, Storage, and Handling

### Reference Section 01 6600Product Storage and Handling Requirements.

### Follow manufacturer’s instructions.

## Warranty

### Provide manufacturer’s standard two year warranty.

### Inspection, Maintenance and Testing:

#### Perform minimum annual inspection and testing on each fire and smoke containment system as required by NFPA 80, manufacturer’s warranty, and as otherwise required by the local authority having jurisdiction.

#### Provide inspection and test documentation.

# Products

## Manufacturer

### Cornel Model SmokeShield™ Fire & Smoke

### Manufacturer:

#### CornellCookson, 24 Elmwood Drive, Mountain Top, PA 18707 www.cornellookson.com

### Label each fire and smoke containment system with following information:

#### Manufacturer’s name.

#### Label of listing agency.

#### Fire protection rating.

#### Air leakage label

## Performance Requirements

### Fire Protection rating tested and labeled to UL10D 3hr.

### Air Leakage:  Not to exceed 3 cfm (0.001416 m3/s) per sf of door opening at 0.1 in (25 Pa) water pressure differential at ambient temperature and 400 degrees F (204 degrees C) tested and labeled to UL 1784 per IBC 2006, 2009, and 2012

## Components

### Construct the curtain head box from 20 gauge structural components with a 24 gauge pre finished galvanized steel cover.

### Provide a removable headbox cover allowing full width access to the assembly and curtain.

### Standard head box sizes will include standard upset and require 11” overall headroom for single curtain/barrel assemblies in openings to 16’x 11’; 12” for openings to 16’x16’, and 13” for openings to 16’x20’.

### **Note to Specifier: Headbox may be mounted above the finished ceiling or below.**

### Headbox Finish: [Standard powder coated finish] [Custom powder coat color as selected by architect].

### **Note to Specifier: Guides are mounted face of wall exposed or hidden under sheetrock, wood or masonry fascia. Please coordinate finish selection with manufacturer and specify accordingly. Please select desired guide finish below**

### Guides: Provide14 GA cold rolled steel [standard powder coat] [custom powder coat] [field painted] to match [ceiling] [header] [fascia] finish. Size: 3-5/8 inches (57.2 mm) wide; 1-3/4 inch.

### Provide guide assemblies that expose no visible fasteners or shadow lines.

### Provide bottom bar composed of steel shapes sufficient to prevent deflection during a fire event and to blend into surrounding finishes where specified with [standard powder coat] [field painted] to match [ceiling] [header] [fascia] finish.

### Provide a barrel constructed of steel tubing of sufficient geometry to limit deflection to less than 1/32” per foot of opening width.

### Provide intermediate support rollers capable of preventing barrel deflection into the opening under the extreme heat conditions of a fire event as a UL listed component.

### Provide a tubular shaped motor residing within the barrel that includes a 115 volt A.C. motor, planetary gearbox assembly, failsafe release mechanism and centrifugal governor.

### Provide a tubular motor assembly constructed of all-metallic components that will not sustain flame or contribute to combustion during a fire event.

### Provide a flush mount key switch to operate the curtain open and closed.

### Provide a motor controller housed in a steel enclosure that may be mounted in numerous positions or locations for maximum versatility.

### **Note to Specifier: Battery backup is recommended to prevent nuisance curtain closures when temporary power outages occur**

### [Provide a battery backup system to prevent curtain deployment during power outages for up to 8 hours.]

### Provide an integral centrifugal governing system that does not require battery or electrical power, and controls curtain descent to 8” – 12” per second.

### Provide curtain material as tested and listed that includes F-920 filament fiberglass with stainless steel wire reinforcement.

# Execution

## Examination

### Examine substrates upon which work will be installed.

#### Verify related work performed under other sections is complete and in accordance with Shop Drawings.

#### Verify wall surfaces and Fire & Smoke door frames are acceptable for installation of system components.

### Coordinate with responsible entity to perform corrective work on unsatisfactory substrates.

## INSTALLATION

### Install smoke and fire system components in accordance with manufacturer’s installation instructions.

## Field Quality Control

### Field Test: Follow manufacturer’s cycle test procedures.

#### Notify Owner’s Representative, local Fire Marshal, alarm sub-contractor and [Fire & Smoke sub-contractor] [Fire & Smoke service company] minimum one week in advance of scheduled testing.

#### Complete inspection and drop test documentation.

## Demonstration

### Demonstrate required testing and maintenance procedures to Owner’s Representative.

### Maintenance and Testing:

#### Perform minimum annual inspection and drop testing on each unit as required by the manufacturer’s warranty, NFPA 80, or under direction of the local authority having jurisdiction.

#### Retain a record of tests per NFPA 80.

End of Section